## pdf
Fuel Leak Detection Wire Model-LFP7000 Specification
Product Name : | Fuel Leak Detection Wire
Model : | P-LFP7000
Product Features
Cable Diameter : | 13 mm (0.52 in) nominal
Cable diameter: | 8 mm (0.32 in) nominal
connector
Cable weight: | 7.3 kg/100 m nominal (4.81 lb/100 ft nominal)
Fluoropolymer braid: | Color - red white and black
Operating temperature: | –20°C to 60°C (–4°F to 140°F)
range
Pull force limit: | Not to exceed 22.7 kg (50 lb)
Bend radius: | 50 mm (2 in) minimum
Pressure: | Loads greater than 9 kg (20 lb) per linear inch at 20°C (68°F) may immediately trigger an alarm
Nonresettable: | Must be replaced after exposure to hydrocarbon liquids
Chemical resistance
Cable functions normally Sulfuric acid (10%)
After exposure in Hydrochloric acid (10%)
accordance with ASTM D Nitric acid (10%)
543 at 23°C (73°F) for Sodium hydroxide (10%)
Sensing cable Less than 10μA leakage when immersed in salt water for 90 days
Connector system Less than 10 μA leakage when immersed in water at 10 psig for 24 hours
Response time
Represented materials | Typical response time at
Hydrocarbon Fuel Type | 20°C (68°F)
Gasoline | ~2 Mins
Diesel Oil | ~3 Mins
Kerosene | ~30 Secs
Light Crude Oil | ~8Mins
Heavy Crude oil | ~16Mins
Reused Time | Can be reused for 3 times,Should be cleaned by factory after using